## Slide 1
FY M.Tech Computer Science & Engineering (DCSE)
UNIT 2: Data Centre Electrical Infrastructure Engineering
Comprehensive Lecture & Examination Master Deck (6-Hour Curriculum)
Key Modules Covered: 1. Utility Power Systems & Substations | 2. Backup Power & UPS Systems 3. Power Distribution Architectures (SLD) | 4. Earthing & Lightning Protection 5. Electrical Design Methodology & Sizing | 6. University Exam Questions & Numericals
MIT World Peace University (MIT-WPU) × NIRVAA Solution Pvt. Ltd. | Academic Year 2026–27

## Slide 2
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 2 of 22
CURRICULUM MAP
Unit 2 Syllabus Breakdown & 6-Hour Pedagogical Framework
Structured module-by-module alignment from utility grid connection down to server silicon
02
Hour 1: Utility Power
MODULE 1
• Grid Entrances: HV/MV Substations (33kV / 11kV).
• Dual Utility Feeds: Diverse routing & substations.
• Step-Down Transformers: Cast Resin vs Oil-immersed.
• Switchgear & RMU: Ring Main Unit protection.
• Power Quality: APFC, THD limits & IEEE 519.
Hour 2: Backup Power
MODULE 2
• Diesel Generators (DG): Standby vs DCC ratings.
• Fuel Autonomy: Day tanks & bulk storage (48-72h).
• Paralleling Controls: Auto-synchronization panels.
• UPS Topologies: Online Double Conversion (VFI).
• Batteries: VRLA vs Li-Ion vs Flywheel ride-through.
Hour 3: Power Distribution
MODULE 3
• Single Line Diagram: Substation to server PSU.
• Power Distribution Units: K-factor isolation transformers.
• RPP vs Track Busway: Overhead modular tap-offs.
• Rack PDUs: Basic, Metered, Monitored & Switched.
• Dual-Corded Servers: Feed A & B redundancy.
Hour 4: Earthing & LPS
MODULE 4
• Grounding Philosophies: Personnel safety & EMC.
• TN-S System: Separate Neutral & PE conductors.
• Signal Reference Grid: 2ft x 2ft underfloor mesh.
• Earth Pits: Chemical earthing (< 1.0 Ohm).
• Surge Protection: Type 1, 2, 3 cascaded SPDs.
Hours 5-6: Design & Exam
MODULE 5
• Tier Standards: Tier I to IV electrical topologies.
• Sizing Methodology: IT kW to facility kVA sizing.
• Metrics: PUE, DCiE & Water Usage (WUE).
• Solved Numericals: UPS battery & transformer math.
• Exam Prep: 15-mark essay questions & answers.

## Slide 3
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 3 of 22
UTILITY POWER
Utility Power Intake: High Voltage Substations & Dual Feeds
Establishing the first line of electrical defense for Tier III/IV high availability
03
Utility Grid Intake Architecture
INFRASTRUCTURE
• Voltage Levels: Medium/High Voltage (132 kV, 66 kV, 33 kV or 11 kV) stepped down to 415V 3-phase.
• Dual Utility Substations: Independent transmission substations originating from diverse grid power stations.
• Diverse Trench Routing: Utility cables enter through physically separated building entrances (> 20 meters apart) to eliminate single-point trench cuts.
• Ring Main Unit (RMU): Provides automated loop isolation; if one feeder faults, the loop automatically re-energizes via alternate switchgear.
• Gas Insulated Switchgear (GIS): Preferred for compact urban DCs over Air Insulated Switchgear (AIS) due to reliability and footprint.
• Exam Tip: In Tier III/IV design, dual utility is best practice, but Uptime Institute considers utility an economic convenience; DGs are the true primary power.
Transformers & Switchgear Engineering
TRANSFORMERS
• Cast Resin (CRT) Dry-Type: Standard indoor choice. Non-flammable, self-extinguishing, zero oil spill risk, maintenance-free.
• Oil-Immersed Transformers (ONAN/ONAF): Higher efficiency for mega-watt substations, but requires outdoor blast-proof blast walls & oil drainage pits.
• K-Factor Rating: Crucial for DC loads. Non-linear server PSUs generate severe 3rd, 5th, 9th harmonics. Transformers MUST be K-13 or K-20 rated to prevent core overheating.
• Impedance Voltage (%Z): Typically 5% to 7% to balance fault-current limitation with minimal voltage drop on sudden load steps.
• Vector Group: Dyn11 (Delta primary, Star secondary with neutral brought out, 30 deg lead) provides essential neutral derivation and traps 3rd harmonics.

## Slide 4
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 4 of 22
POWER QUALITY
Power Quality Engineering, Harmonics & Power Factor
Mitigating non-linear load anomalies to protect data centre efficiency and compliance
04
Power Quality Distortions & Solutions
STANDARDS: IEEE 519
• Voltage Sags & Swells: Short-duration RMS voltage drops/rises caused by grid faults or heavy motor starts. Cleared by UPS battery inverter buffers.
• Harmonics (THD): Caused by Switch Mode Power Supplies (SMPS) in servers drawing non-sinusoidal current pulses.
• Triplen Harmonics: 3rd, 9th, 15th harmonic currents do not cancel out in the neutral; they add up, causing neutral conductor overheating ($I_{neutral} > 1.73 \times I_{phase}$).
• Active Harmonic Filters (AHF): Injects counter-phase harmonic currents in real-time, maintaining Total Harmonic Distortion (THDi) < 5% as per IEEE 519.
• Automatic Power Factor Correction (APFC): Modern server PSUs feature Active PFC (PF > 0.98), but legacy cooling inductive motors require capacitor banks with detuned reactors.
Transfer Mechanisms: ATS vs. STS Comparison
HIGH EXAM YIELD
• Automatic Transfer Switch (ATS): Electromechanical switch with mechanical interlock. Typical break-before-make transfer time: 50 ms to 100 ms.
• Static Transfer Switch (STS): Solid-state SCR (Silicon Controlled Rectifier) thyristor-based switch. Ultra-fast sub-cycle transfer time: 2 ms to 4 ms.
• ITIC / CBEMA Curve Compliance: Server power supplies survive power loss for only 16 ms to 20 ms (hold-up time of bulk capacitors).
• Application of ATS: Used upstream between Utility and Diesel Generator feeds (where UPS bridges the 10-15 second transition).
• Application of STS: Used downstream near the IT racks for seamless phase-synchronized transfer between Feed A and Feed B without server reboot.
• Exam Comparison: ATS has moving parts and wear; STS has no moving parts, instantaneous transfer, but higher continuous thermal dissipation.

## Slide 5
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 5 of 22
BACKUP POWER
Backup Power Generation: Diesel Generator (DG) Sets & Fuel Autonomy
The true primary power source according to Uptime Institute Tier certification
05
DG Ratings & Sizing Criteria (ISO 8528-1)
ISO 8528 RATINGS
• Standby Power Rating (ESP): Maximum power for emergency duration; limited to 200 hours/year at 70% average load. (Not acceptable for Tier III/IV).
• Continuous Operating Power (COP): Continuous base load without interruption for unlimited hours.
• Data Centre Continuous (DCC) Rating: Vendor certification (e.g. Cummins, Caterpillar) allowing continuous operation at 100% rated load for unlimited hours.
• Step Load Acceptance: Modern DG engines must accept 100% single-step block load within NFPA 110 Type 10 standards (cranks and accepts full load in < 10 seconds).
• Electronic Governors: Isochronous frequency control (maintains 50 Hz ± 0.25% regardless of IT load fluctuations).
• Auxiliary Systems: Dual redundant starting electric motors with separate battery banks, jacket water heaters (40°C pre-heat), redundant fuel lift pumps.
Fuel Storage & Paralleling Switchgear
72-HOUR AUTONOMY
• Day Tank: Local fuel tank inside acoustic generator room holding 1 to 2 hours of fuel for immediate engine gravity feed.
• Bulk Fuel Storage: Underground or double-walled aboveground storage tanks sized for 48 to 72 hours of continuous full-load operation (Tier III/IV requirement).
• Fuel Polishing Systems: Automated filtration removing water, sediment, and microbial growth to prevent injector fouling during emergency starts.
• Paralleling Switchgear (PSG): Automatically synchronizes multiple generator outputs (voltage, frequency, phase angle) onto a common bus.
• Load Shedding & Add Logic: Progressively adds non-critical loads (HVAC chillers -> CRAH units -> battery chargers) to prevent engine stalling.
• Black Start Capability: Ability to start and stabilize the entire facility without any external grid assistance.

## Slide 6
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 6 of 22
BACKUP POWER
Uninterruptible Power Supply (UPS) Topologies & Architecture
The zero-interruption bridge between utility loss and generator stabilization
06
Online Double Conversion (VFI)
INDUSTRY STANDARD
• Classification: IEC 62040-3 VFI (Voltage & Frequency Independent).
• Operation: Rectifier converts AC to DC; Inverter continuously reconverts DC to clean AC.
• Transfer Time: Exactly 0 ms (seamless continuous DC bus supply).
• Static Bypass: Ultra-fast thyristor bypass switch in case of internal inverter failure or overcurrent.
• Maintenance Bypass: Manual wrap-around switch allowing complete physical isolation for servicing.
• Efficiency: 95% - 97% in true double conversion; up to 99% in ECO mode.
• Verdict: The global standard for enterprise & cloud data centres.
Rotary / Dynamic UPS (DRUPS)
ROTARY / DRUPS
• Working: Integrates diesel engine, kinetic energy flywheel, and synchronous motor-generator on a common shaft.
• Operation: During utility failure, spinning flywheel supplies kinetic energy for 15-30s while diesel engine clutches and fires up.
• Advantages: Eliminates chemical battery rooms, zero HVAC required for batteries, massive short-circuit clearing capability.
• Disadvantages: Higher maintenance, mechanical wear, louder noise, higher initial capital cost, short ride-through window.
• Application: Heavy industrial, European banking DCs, sites with extreme temperature conditions.
Line Interactive & Standby
UNSUITABLE FOR DCS
• Standby (Off-line / VFD): Inverter is idle; load fed by raw utility. Transfer time: 6-12 ms. Unsuitable for mission-critical enterprise DCs.
• Line Interactive (VI): Bi-directional inverter with buck-boost transformer. Transfer time: 4-8 ms.
• Drawbacks: No true frequency isolation, power transients pass through, risk of server PSU drop during transfer.
• Exam Rule: Only Online Double Conversion (Static) and DRUPS (Rotary) qualify for Tier III and Tier IV mission-critical data centres!

## Slide 7
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 7 of 22
ENERGY STORAGE
Energy Storage Technologies: VRLA vs. Lithium-Ion vs. Flywheel
Critical comparison for CAPEX, footprint, thermal safety, and operating lifespan
07
VRLA (Valve Regulated Lead-Acid)
LEGACY TECH
• Chemistry: Absorbed Glass Mat (AGM) or Gel electrolyte lead-acid.
• Service Life: 3 to 5 years (requires frequent cell monitoring).
• Weight & Footprint: Heavy (requires reinforced floor slabs, 800-1000 kg/m²); large dedicated battery rooms.
• Operating Temp: Strict 20°C - 25°C. Every 10°C rise halves battery operational lifespan!
• Maintenance: High maintenance, periodic impedance testing, risk of acid leaks & thermal runaway.
• CAPEX: Lowest initial capital expenditure (traditional baseline).
Lithium-Ion (LFP / NMC)
MODERN CHOICE
• Chemistry: Lithium Iron Phosphate (LFP) preferred for fire safety; NMC for high power density.
• Service Life: 12 to 15 years (matches UPS lifecycle).
• Weight & Footprint: 60% lighter, 70% smaller footprint. Can be colocated directly in IT white space.
• Operating Temp: Tolerant up to 30°C with negligible degradation; reduces battery room cooling energy.
• BMS: Integrated Battery Management System monitors cell voltage, impedance, temperature in real-time.
• CAPEX: 1.5x higher initial cost, but lower TCO over 10-year period due to zero battery replacement.
Kinetic Flywheels
ZERO CHEMICAL
• Mechanism: High-speed rotor (up to 36,000 RPM) spinning in magnetic vacuum bearings.
• Ride-Through: 15 to 30 seconds (purely designed to bridge time until DG reaches nominal voltage & frequency).
• Cycle Life: Unlimited deep-discharge cycles (> 1,000,000 cycles) with zero capacity fading.
• Safety: Zero toxic chemicals, zero fire or thermal runaway hazard, completely recyclable.
• Drawback: No prolonged autonomy. If generator fails to crank in 15 seconds, DC crashes.

## Slide 8
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 8 of 22
REDUNDANCY MODELS
Power Redundancy Architectures: N, N+1, 2N & Distributed
Mathematical and architectural topologies defined by Uptime Institute and TIA-942
08
N System (Basic)
TIER I
• Capacity: Exactly 100% of IT load requirement.
• Redundancy: Zero (0). No backup modules.
• SPOF: Multiple Single Points of Failure throughout path.
• Maintenance: Requires complete DC shutdown for maintenance.
• Cost: Lowest baseline cost (1.0x).
• Tier Level: Tier I.
N+1 System (Parallel)
TIER II
• Capacity: N modules required + 1 extra module for backup.
• Mechanism: Modules share common input & output buses.
• Maintenance: Any single module can be serviced while remaining N modules carry the load.
• Limitation: Distribution bus is still a single point of failure!
• Cost: Approx 1.25x - 1.3x cost.
• Tier Level: Tier II.
2N System (Dual Path)
TIER IV
• Capacity: Two complete independent distribution paths (Path A + Path B).
• Mechanism: Each path can handle 100% of total load. Normal operation: 50% load each.
• Concurrency: Concurrent Maintainability + Fault Tolerance.
• SPOF: Zero single points of failure from grid to rack.
• Cost: Approx 2.0x - 2.2x cost.
• Tier Level: Tier IV.
Distributed (3N/2)
TIER III
• Capacity: 3 UPS modules feed 2 independent load buses (3-to-make-2).
• Efficiency: High utilization factor (66% per unit vs 50% in 2N).
• Stranded Power: Drastically reduces unused stranded capacity.
• Complexity: Complex STS switching and circuit management.
• Cost: Approx 1.5x - 1.6x cost.
• Tier Level: Tier III.

## Slide 9
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 9 of 22
POWER DISTRIBUTION
End-to-End Single Line Diagram (SLD): Substation to Server Chip
Visual breakdown of the electrical distribution hierarchy in a mission-critical facility
09
Data Centre Power Flow Hierarchy & Component Mapping
END-TO-END FLOW
• Level 1: Utility Grid & Generation -> Dual 33kV/11kV Substations + N+1 Diesel Generators (DCC rated) with Auto-Synchronization Switchgear.
• Level 2: Main MV/LV Switchboard & ATS -> Automatic Transfer Switch selects Utility or Generator; feeds main low voltage switchboards (415V, 3-phase).
• Level 3: Centralized UPS System -> 2N Dual Independent UPS plants (System A & System B) with dedicated battery banks (VRLA or Li-Ion).
• Level 4: Power Distribution Units (PDUs) -> Stepped down / conditioned power via K-20 isolation transformers; integrated Branch Circuit Monitoring (BCMS).
• Level 5: Overhead Busway / RPP -> Modular overhead busbars with hot-swappable tap-off boxes feeding individual server racks.
• Level 6: Rack Power Distribution (ePDU) -> Dual intelligent rack PDUs (ePDU A and ePDU B) per cabinet; feeds redundant server power supply units (PSUs).
• Level 7: Server Dual PSUs -> Server Power Supply 1 (A-Feed) and Power Supply 2 (B-Feed) convert 230V AC to 12V DC / 48V DC on server motherboard.
• Exam Tip: In your exam SLD diagram, always draw BOTH paths (A & B feeds) completely isolated with cross-tie breakers and STS indicated!

## Slide 10
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 10 of 22
POWER DISTRIBUTION
Floor Distribution: PDUs, RPPs vs. Overhead Busway Systems
Transitioning from underfloor cable whips to modular, flexible overhead bus ducts
10
Power Distribution Units (PDUs) & RPPs
TRANSFORMER PDU
• PDU Function: Acts as the primary power gatekeeper for server rows. Includes main circuit breaker, isolation transformer, and sub-feed panels.
• Isolation Transformer: Delta-Wye (Dyn11) transformer steps down voltage, creates clean local neutral ground bond, and blocks common-mode noise.
• Remote Power Panels (RPP): Secondary panel boards dedicated solely to circuit breakers without an isolation transformer.
• Branch Circuit Monitoring System (BCMS): Meters voltage, current, active power (kW), energy (kWh), and power factor per individual circuit breaker.
• Traditional Underfloor Cabling: Flexible conduit whips routed beneath raised floor. Major drawback: cable nests obstruct cold air airflow from CRAC units.
Overhead Track Busway Systems (Modern)
MODERN BUSWAY
• Concept: Continuous modular aluminum/copper busbar track suspended above server rack rows (eliminates underfloor whips entirely).
• Hot-Swappable Tap-Off Boxes: Plugs into the overhead track while live without cutting power to adjacent racks; customizable with breaker sizes (16A, 32A, 63A).
• Footprint Savings: Frees up 100% of white space floor footprint previously occupied by bulky floor-standing RPPs.
• Airflow Optimization: Clear underfloor plenum allows laminar cold air distribution; directly improves cooling efficiency and lowers PUE.
• Flexibility & Scalability: Rapid deployment for tenant moves, adds, and changes (MAC) in cloud colocation facilities.
• Exam Tip: Always cite Overhead Busway as the modern replacement for RPPs due to airflow, modularity, and zero stranded floor space.

## Slide 11
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 11 of 22
RACK POWER
In-Rack Power Distribution: Intelligent ePDUs & Dual-Corded Servers
Ensuring 2N server-level availability and granular energy metering
11
Rack PDU Categories
RACK PDU TYPES
• Basic PDU: Simple power strip distributing reliable power; zero metering or network intelligence.
• Metered PDU: Digital display showing total aggregate current (Amps); prevents breaker tripping overloads.
• Monitored PDU: Network-enabled (SNMP/HTTP); measures input phase voltage, current, kWh, and power factor remotely.
• Switched PDU: Individual outlet-level metering plus remote power switching (reboot frozen servers remotely without physical site visit).
• High-Density 3-Phase: 415V 32A/63A 3-phase rack PDUs delivering 22 kW to 43 kW per rack for AI/GPU clusters.
Dual-Corded Server Architecture
DUAL CORDING
• Dual Power Supplies (PSU): Enterprise servers incorporate two independent power supplies (PSU 1 and PSU 2).
• Redundant Connection: PSU 1 connects to Rack PDU A (from UPS Path A); PSU 2 connects to Rack PDU B (from UPS Path B).
• Load Sharing: PSUs operate in active/active load-sharing mode (each carries 50% load under normal conditions).
• Instant Failover: If Path A completely drops, PSU 2 instantaneously carries 100% load with zero server disruption.
• Single-Corded Exception: Legacy gear with single power cord requires a Rack-mount ATS (rATS) to achieve dual-path feed.
Rack Safety & Cable Management
BEST PRACTICES
• Locking Connectors: IEC C13 / C14 and C19 / C20 locking plugs prevent accidental dislodgement during rack maintenance.
• Color-Coded Cables: Industry standard practice: Red/Black for Feed A power cables, Blue/Grey for Feed B power cables.
• Thermal Separation: Power cables segregated from network fiber/copper cables in overhead ladder racks to avoid inductive EMI noise.
• Derating Rule: Continuous circuit loads must not exceed 80% of circuit breaker rating (e.g. 16A breaker max continuous load = 12.8A) as per NEC / IEC rules.

## Slide 12
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 12 of 22
EARTHING & GROUNDING
Data Centre Earthing Philosophies & The TN-S Grounding Scheme
Guaranteeing human life safety, clearing fault currents, and eliminating electrical noise
12
Three Pillars of Data Centre Grounding
IEEE 1100 EMERALD
• Pillar 1 - Safety Grounding (PE): Low-impedance path to earth to clear short-circuit faults instantly via protective circuit breakers; limits touch voltage to safe levels (< 50V).
• Pillar 2 - System Grounding: Grounding the transformer star neutral to stabilize phase-to-ground voltages under normal and transient conditions.
• Pillar 3 - High-Frequency Signal Grounding: Providing an equipotential ground plane for microelectronic logic reference, shielding against RFI, EMI, and ESD transients.
• Standard Reference: IEEE 1100 ('Emerald Book' - Recommended Practice for Powering and Grounding Electronic Equipment).
• Earth Resistance Requirement: Commercial buildings allow 5.0 Ohms. Data centres strictly mandate < 1.0 Ohm (target < 0.5 Ohm for mission-critical).
Why TN-S Grounding is Mandatory for DCs
MANDATORY SCHEME
• TN-S Definition: Terre-Neutre Séparé (Separate Neutral and Protective Earth conductors throughout the entire electrical network).
• Single Point of Neutral-Earth Bond: N and PE are bonded ONLY at the secondary of the main incoming transformer or PDU; NEVER bonded downstream!
• Danger of TN-C (Combined PEN): In TN-C, 3rd harmonic server neutral currents travel along the equipment metallic chassis, causing electric shock hazards and catastrophic data packet corruption.
• Zero Earth Leakage Current: In TN-S, under normal operating conditions, zero current flows through the PE conductor, ensuring a zero-voltage clean reference.
• Residual Current Devices (RCD): TN-S allows sensitive, reliable operation of earth fault protection devices and ground fault relays.

## Slide 13
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 13 of 22
LPS & SRG
Signal Reference Grid (SRG) & Cascaded Lightning Protection (IEC 62305)
Eliminating high-frequency digital noise and defending against multi-kiloamp lightning strikes
13
Signal Reference Grid (SRG) Architecture
IEEE 1100 / SRG
• What is SRG? A prefabricated copper strip grid (typically 2 ft × 2 ft mesh) laid directly beneath the raised floor tiles in the server room.
• High-Frequency Physics: At 50 Hz power frequency, a single grounding cable works. At high frequencies (MHz/GHz clock harmonics), a single wire acts like an antenna due to high inductive reactance ($X_L = 2\pi f L$).
• Mesh Principle: A 2 ft × 2 ft mesh provides thousands of parallel paths, drastically reducing impedance ($Z \rightarrow 0$) at high frequencies.
• Bonding Protocol: Every server cabinet, PDU chassis, overhead cable tray, and raised floor stanchion is bonded to the SRG using short, flat braided copper straps.
• Benefits: Eliminates ground loops, dissipates static ESD, and stops data corruption between interconnected servers.
Cascaded Lightning Surge Protection (IEC 62305)
IEC 62305 / SPDS
• External Lightning Protection System (LPS): Faraday cage mesh on roof + air termination rods + low-inductance down conductors + ring earth electrode.
• Type 1 (Class I) SPD: Installed at main incoming service entrance switchgear. Tested with 10/350 µs lightning waveform; discharges direct strike currents ($I_{imp} \ge 25\text{ kA}$).
• Type 2 (Class II) SPD: Installed at sub-distribution boards and UPS input/output switchboards. Tested with 8/20 µs waveform ($I_n \ge 20\text{ kA}$); clamps residual switching transients.
• Type 3 (Class III) SPD: Installed at PDU branch circuits and Rack PDUs. Clamps fine voltage spikes to < 1.0 kV, safe for sensitive server silicon.
• Coordination Rule: SPDs must be coordinated with minimum cable separation distance or series inductors so Type 1 fires before downstream Type 2/3.

## Slide 14
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 14 of 22
ELECTRICAL DESIGN
Electrical Load Calculation & Sizing Methodology
Step-by-step engineering calculation pipeline from white space rack kW to utility grid kVA
14
Step-by-Step Engineering Sizing Pipeline
SIZING ALGORITHM
• Step 1: Determine Total IT White Space Load (P_IT) -> Calculate total rack count × average rack power density (e.g., 100 racks × 6 kW/rack = 600 kW).
• Step 2: Convert IT Active Power (kW) to Apparent Power (kVA) -> S_IT = P_IT / PF_IT. Assuming modern server PF = 0.98, S_IT = 600 / 0.98 = 612.2 kVA.
• Step 3: Size the UPS Plant -> S_UPS = S_IT / (Efficiency_UPS × Max_Load_Factor). For 96% efficiency and 80% maximum continuous loading: S_UPS = 612.2 / (0.96 × 0.80) = 797 kVA. Select standard rating: 800 kVA or two 500 kVA units in 2N.
• Step 4: Battery Autonomy Calculation -> Sized using battery manufacturer constant-power discharge tables to sustain full UPS inverter DC input for 10-15 minutes at end-of-discharge voltage (1.75V/cell).
• Step 5: Facility Auxiliary & Mechanical Cooling Load -> Mechanical chillers, pumps, fans, lighting, and BMS typically equal 30% to 50% of IT load. Total facility load = P_IT × PUE.
• Step 6: Transformer Sizing (S_Tx) -> S_Tx = Total_Facility_kVA × Diversity Factor × Growth Margin (typically 1.25x). In 2N, each transformer is sized to carry 100% of total facility load alone.
• Step 7: Generator Sizing (S_DG) -> Generator capacity must account for non-linear harmonic heating, UPS battery charging step-load, and motor starting inrush currents (typically 1.3x to 1.5x total load).

## Slide 15
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 15 of 22
ENERGY METRICS
Data Centre Energy Efficiency Metrics: PUE, DCiE & Benchmarks
The universal gold standards for measuring data centre infrastructure sustainability
15
PUE & DCiE Mathematical Formulations
THE GREEN GRID
• Power Usage Effectiveness (PUE): Defined by The Green Grid as the ratio of total energy entered into the facility to energy consumed by IT computing equipment.
• PUE Formula: PUE = Total Facility Energy / IT Equipment Energy.
• Total Facility Energy includes: IT equipment + Chillers + CRAH units + Fans + Pumps + Transformer losses + UPS losses + PDU losses + Lighting + Security.
• Ideal PUE: Exactly 1.0 (means 100% of power goes into servers; 0% wasted on cooling or electrical losses).
• Data Centre Infrastructure Efficiency (DCiE): The reciprocal percentage metric: DCiE = (IT Equipment Power / Total Facility Power) × 100% = (1 / PUE) × 100%.
Industry Benchmarks & Efficiency Levers
BENCHMARKS
• Legacy Data Centre (Historic): PUE 2.0 (DCiE 50%) -> For every 1 kW used by servers, 1 kW is wasted on cooling and electrical losses!
• Modern Enterprise Data Centre: PUE 1.3 to 1.4 (DCiE 71% to 77%) -> High-efficiency UPS, hot/cold aisle containment, variable frequency drives (VFD).
• Hyperscale Cloud (Google, AWS, Microsoft): PUE 1.10 to 1.15 (DCiE 87% to 91%) -> Free-air economization, high-voltage rack distribution, direct-to-chip liquid cooling.
• Top Electrical Levers to Lower PUE: 1. Eliminate double transformation steps (e.g. 415V direct to rack). 2. Operate UPS units at > 60% load to remain in peak efficiency curve. 3. Use High-efficiency amorphous core / K-20 isolation transformers.
• Associated Metrics: Water Usage Effectiveness (WUE) & Carbon Usage Effectiveness (CUE).

## Slide 16
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 16 of 22
TIER CLASSIFICATION
Uptime Institute Tier Standards: Electrical Requirements
Analyzing Tier I through Tier IV electrical concurrency and fault tolerance
16
Tier I: Basic Capacity
TIER I
• Paths: Single distribution path.
• Redundancy: N (No redundancy).
• UPS / Gen: Dedicated UPS & DG present, but single module.
• SPOF: Multiple single points of failure.
• Concurrent Maintenance: No.
• Annual Downtime: 28.8 hours (99.671% availability).
• Target: Small internal IT rooms.
Tier II: Redundant Comps
TIER II
• Paths: Single distribution path.
• Redundancy: N+1 active components (UPS, DG, Chillers).
• SPOF: Distribution piping & switchboards are still SPOFs.
• Concurrent Maintenance: No (distribution maintenance requires shutdown).
• Annual Downtime: 22.0 hours (99.741% availability).
• Target: Regional businesses.
Tier III: Concurrently Maint.
TIER III
• Paths: Dual paths (1 active, 1 alternate standby).
• Redundancy: N+1 components minimum.
• Concurrent Maintenance: YES! Any component or path can be removed for maintenance without taking IT offline.
• Fault Tolerance: Not fully fault tolerant against unplanned events.
• Annual Downtime: 1.6 hours (99.982% availability).
• Target: Enterprise & Colocation.
Tier IV: Fault Tolerant
TIER IV
• Paths: 2N Dual active simultaneously energized paths (Feed A + Feed B).
• Redundancy: 2(N+1) or 2N throughout.
• Fault Tolerance: YES! System automatically absorbs ANY unplanned failure without IT impact.
• Compartmentalization: Paths physically separated in fire-rated rooms.
• Annual Downtime: 26.3 minutes (99.995% availability).
• Target: Financial & Mission-Critical.

## Slide 17
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 17 of 22
SOLVED NUMERICAL
Exam Numerical 1: UPS & Battery Bank Sizing Problem
Step-by-step mathematical calculation typical of a 10-15 mark university examination problem
17
Numerical Problem & Step-by-Step Solution
10-MARK EXAM PROBLEM
• Problem Statement: A Tier-III Data Centre has an IT white space load of 600 kW with an average Power Factor of 0.95. The facility uses an Online Double Conversion UPS with 95% inverter efficiency. Sizing guidelines mandate that UPS operational load should not exceed 75% of rated capacity under normal operation. The battery system must provide 15 minutes autonomy at full load with 400V DC bus voltage. Calculate: (a) Total IT Apparent Power in kVA, (b) Minimum UPS Rating required in kVA, (c) Battery Bank Ampere-Hour (Ah) capacity required.
• Part (a) - IT Apparent Power Calculation: Formula: S_IT = P_IT / PF = 600 kW / 0.95 = 631.58 kVA.
• Part (b) - UPS Sizing Calculation: Accounting for 95% inverter efficiency: P_DC_input = 600 kW / 0.95 = 631.58 kW. Applying 75% operational cap factor: S_UPS_minimum = 631.58 kVA / 0.75 = 842.1 kVA. Design Recommendation: Select two 500 kVA UPS units in an N+1 parallel redundant configuration (Total capacity = 1000 kVA; normal load per unit = 42.1%, well within the 75% threshold).
• Part (c) - Battery Bank Ah Capacity Calculation: DC Input Power required from battery: P_battery = 631.58 kW = 631,580 Watts. Discharge Current (I_dc): I_dc = P_battery / V_DC_bus = 631,580 W / 400 V = 1578.95 Amperes. Battery Energy Required for 15 minutes (0.25 hours): Energy = 1578.95 A × 0.25 h = 394.74 Ah. Applying 1.25 Aging & Temperature Derating factor: Required Battery Capacity = 394.74 Ah × 1.25 = 493.4 Ah. Exam Conclusion: Specify a 400V DC Battery Bank with minimum 500 Ah rating (or two parallel strings of 250 Ah cells).

## Slide 18
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 18 of 22
SOLVED NUMERICAL
Exam Numerical 2: Total Facility Power & PUE Sizing
Comprehensive power budgeting and generator sizing for enterprise data centres
18
Numerical Problem & Step-by-Step Solution
10-MARK EXAM PROBLEM
• Problem Statement: A cloud data centre hosts 200 server racks with an average density of 5 kW per rack. The facility operates at a design PUE of 1.35. The mechanical cooling system accounts for 75% of the total non-IT overhead energy, while electrical distribution losses and lighting account for the remaining 25%. Calculate: (a) Total IT Load in kW, (b) Total Facility Load in kW, (c) Cooling Power Consumption in kW, (d) Minimum Transformer Sizing (kVA) with 20% safety margin and 0.92 facility power factor, (e) DCiE percentage.
• Part (a) - Total IT Load: P_IT = 200 racks × 5 kW/rack = 1,000 kW (1.0 MW).
• Part (b) - Total Facility Load: Formula: Total Facility Load = P_IT × PUE Total Facility Load = 1,000 kW × 1.35 = 1,350 kW (1.35 MW).
• Part (c) - Overhead & Cooling Power: Total Overhead Loss = Total Facility Load - P_IT = 1,350 kW - 1,000 kW = 350 kW. Cooling Power = 75% of Overhead = 0.75 × 350 kW = 262.5 kW. Electrical Losses & Lighting = 25% of Overhead = 0.25 × 350 kW = 87.5 kW.
• Part (d) - Transformer Sizing in kVA: Facility Apparent Power = Total Facility kW / Facility PF = 1,350 kW / 0.92 = 1,467.39 kVA. Applying 20% safety & future growth factor: S_Tx = 1,467.39 kVA × 1.20 = 1,760.87 kVA. Standard Engineering Selection: Select 2,000 kVA (2 MVA) Cast Resin Dry-Type Transformer. In Tier III/IV 2N configuration: Install two 2,000 kVA transformers (Path A & Path B).
• Part (e) - Data Centre Infrastructure Efficiency (DCiE): DCiE = (1 / PUE) × 100% = (1 / 1.35) × 100% = 74.07%.

## Slide 19
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 19 of 22
EXAM REVISION
High-Yield Comparison Tables for Rapid Exam Revision
Key distinction tables frequently asked in 5-mark short note questions
19
ATS vs. STS Comparison (5 Marks)
ATS VS STS
• Feature / ATS / STS
• Switching Mechanism: Electromechanical contactor vs Solid-state SCR thyristor.
• Transfer Time: 50 ms to 100 ms (break-before-make) vs 2 ms to 4 ms (sub-cycle).
• Server Impact: Causes server reboots without UPS vs completely seamless (< 16ms ITIC curve).
• Mechanical Wear: Contacts degrade over time vs zero moving parts (infinite cycles).
• Heat Dissipation: Negligible heat loss vs continuous thyristor forward voltage drop heat.
• Cost: Significantly lower cost vs higher capital cost.
• Typical Location: Upstream between Utility and Generator vs Downstream between Dual UPS Feeds.
VRLA vs. Lithium-Ion Batteries (5 Marks)
VRLA VS LI-ION
• Parameter / VRLA / Lithium-Ion (LFP)
• Lifespan: 3 to 5 years vs 12 to 15 years.
• Weight & Space: Very heavy (requires reinforced slabs) vs 60% lighter, 70% smaller footprint.
• Temperature Sensitivity: Extreme (every 10°C rise halves life) vs high thermal tolerance up to 30°C.
• Cycle Life: 200 - 400 deep cycles vs 2,000 - 3,000 deep discharge cycles.
• Monitoring: Manual / periodic impedance vs automated integrated BMS (Battery Management System).
• CAPEX vs OPEX: Lower initial CAPEX, high replacement OPEX vs higher CAPEX, drastically lower 10-yr TCO.
• Thermal Runaway Risk: Moderate (acid leakage / drying) vs mitigated via LFP chemistry + smart BMS cutoffs.

## Slide 20
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 20 of 22
EXAM BLUEPRINT
Frequently Asked University Exam Questions & Answer Blueprints
Model structured answers and diagrams required for maximum marks
20
15-Mark Question 1: Single Line Diagram (SLD)
ESSAY QUESTION 1
• Question: 'Draw the complete Single Line Diagram (SLD) of a Tier-IV Data Centre electrical distribution system from incoming utility to server rack. Explain the role of each component.'
• Marking Breakdown & Key Scoring Points: 1. Neat Dual-Path Schematic (5 Marks): Draw Utility Feeds A & B, Substation Transformers, DGs, ATS, 2N UPS, PDUs, Busways, and Dual-Corded Server PSUs. 2. Component Functionality (5 Marks): Explain RMU, K-20 Isolation Transformer, Static Bypass, and Branch Circuit Monitoring. 3. Concurrency & Fault Tolerance (5 Marks): State why 2N eliminates all SPOFs and how any component can be removed live without IT downtime.
10-Mark Question 2: Online Double Conversion UPS
ESSAY QUESTION 2
• Question: 'With a neat block diagram, explain the operation of an Online Double Conversion UPS. Explain the functions of the Rectifier, Inverter, Static Bypass, and Manual Bypass.'
• Marking Breakdown & Key Scoring Points: 1. Block Diagram (4 Marks): Draw AC Input -> Rectifier/Charger -> Battery Bank DC Bus -> Inverter -> Load, with Static Bypass & Maintenance Bypass loops. 2. Operating Modes (4 Marks): Describe Normal Mode (Double conversion), Battery Mode (Inverter fed by battery upon utility loss, 0 ms transfer), and Static Bypass Mode (fault/overload). 3. Advantages (2 Marks): Full voltage & frequency stabilization (VFI), zero transfer time, harmonic isolation.

## Slide 21
M.Tech CSE · Data Centre Systems Engineering | Unit 2: Electrical Infrastructure Engineering | Slide 21 of 22
EXAM BLUEPRINT
Frequently Asked University Exam Questions & Answer Blueprints
Model structured answers and diagrams required for maximum marks
21
10-Mark Question 3: Earthing & SRG Scheme
ESSAY QUESTION 3
• Question: 'Explain the earthing and lightning protection scheme required for a modern enterprise data centre. Why is a Signal Reference Grid (SRG) necessary under raised floors?'
• Key Scoring Points for Full Marks: • Define the TN-S earthing scheme and why neutral & protective earth must NEVER be bonded downstream. • Explain the limitation of single ground wires at high clock frequencies ($X_L = 2\pi f L$) vs the 2 ft × 2 ft copper mesh SRG providing zero inductive impedance. • Describe the 3-stage cascaded Surge Protection Device (SPD) coordination (Type 1 at intake, Type 2 at distribution, Type 3 at rack). • State the earth pit resistance limit (< 1.0 Ohm) as per IEEE 1100.
5-Mark Short Notes Master Checklist
SHORT NOTES
• Expected 5-Mark Short Notes: 1. 'Data Centre Continuous (DCC) Generator Rating vs Standby Rating' 2. 'Overhead Track Busway System vs Traditional Underfloor RPPs' 3. 'Power Usage Effectiveness (PUE) and methods to improve it' 4. 'Static Transfer Switch (STS) operating principle and CBEMA curve' 5. 'K-Factor Transformers and Triplen Harmonic Mitigation'
• Golden Exam Rule: Every 5-mark answer must have: (1) Definition/Formula, (2) Labeled block diagram or circuit, (3) 4 to 5 crisp bulleted features, (4) Practical Data Centre example!

## Slide 22
UNIT 2: SUMMARY & HIGH-YIELD TAKEAWAYS
Master these 5 core concepts to score 100% in your Unit 2 Examination
1. The Power Chain
FLOW
• Utility (11/33kV) -> RMU -> K-Factor Transformer -> ATS -> UPS (2N) -> PDU -> Overhead Busway -> Rack ePDU -> Server Dual PSUs.
• Remember: Uptime Institute treats the DG plant as the primary continuous source!
2. 2N vs N+1
REDUNDANCY
• N+1 provides component redundancy on a shared bus (Tier II).
• 2N provides two completely isolated, concurrently maintainable, fault-tolerant active paths (Tier IV).
• Dual-corded servers are essential to leverage 2N.
3. Clean Grounding
SAFETY & EMC
• TN-S system is mandatory (separate Neutral and Earth).
• Signal Reference Grid (SRG) 2ft x 2ft mesh under raised floor stops MHz high-frequency noise.
• Cascaded SPDs: Type 1 -> Type 2 -> Type 3.
• Ground resistance < 1.0 Ohm.
4. Key Math Formulas
FORMULAS
• PUE = Total Facility kW / IT kW.
• DCiE = (1 / PUE) × 100%.
• IT kVA = IT kW / Power Factor.
• Battery Ah = (P_dc / V_dc) × Hours × 1.25 aging factor.
• Tx kVA = Facility kVA × Diversity × 1.25 margin.